## Slide 1: Periodic Wind Disturbance Rejection using Robust Individual Control Strategy
Mar 5, 2018
Department of Mechanical Engineering
University of Connecticut
Storrs, CT, USA
Yuan Yuan, X. Chen, J. Tang
Photo by NREL

## Slide 2: Outline
Background
Motivation
Proposed Robust Control Method
Results
Concluding Remarks

## Slide 3
Wind Energy
Fastest growing renewable energy source in the world: The worldwide wind capacity reached over 400,000 MW by the end of 2015
Low cost & environmentally friendly
Wind turbine control loops
  Generator torque control
  Blade pitch control
  Nacelle yaw control
Pitch control animation
Yaw control animation
Background: Wind Turbine and Control
Notes: It is well known that wind energy is the fastest ….
It is also low cost
One important aspect of wind turbine is the control system. Let us look at the control mechanism of a typical wind turbine
The blade has a lot of airfoil cross-sections consisting of different sizes and shapes from the root to tip, the simple airfoil technology makes the wind turbine blade turn, a lift force is produced when a fluid moves over an airfoil.
The wind turbine blades typically turn at a very low speed due to the noise and mechanical strength, considering this low speed rotation we canot produce any meaning electricity frequency from the generator. So before connecting to the generator, the speed is increased in a gearbox.
There are 3 separate loops here. The first one is ….
In this research I focus on … which are most commonly studied in high wind speeds
//generator change the frequncey
Hydraulic pitch torque control: applying torque on the generator
Yaw: wind turbine be alligened with the wind direction

## Slide 4: Outline
Background
Motivation
Proposed Robust Control Method
Concluding Remarks
Future Tasks

## Slide 5: Blade pitch control
Collective pitch control animation
Collective pitch control:
All three blades move in the same angle
Regulate power and speed
Mitigate symmetric loads due to uniformly distributed wind
Blade failure
Why do we control wind turbine pitch angle?
Power(W)
Wind speed (m/s)
3
11.4
25
Power regulation

## Slide 6: Motivation1
Individual pitch control to mitigate periodic loads
Enabled by recent hardware advancements
wind
wind
upwind turbine
downwind turbine
Tower shadow
Tower top
, : prevailing wind speed at the tip of each blade
Wind shear
Tower shadow and wind shear effects
Periodic loads
different wind speed at different height
Notes: In our previous study, we only use collective pitch control to acheive load mitigation. All blades pitch at the same angle. So only the Symmetricl loads can be reduced. But, in practical wind turbine applications, periodic loads are inevitable that need our attention.
The concept of tower shadow is illustrated in these two figures.
there is a significant difference between these situations.
In the left figure, the wind passes through blade first and then tower.
In the right figure, the wind passes through tower first and then blade. If we see from the tower top, the wind speed is decresed due to the shadow of tower in the right figure.
Wind shear means the wind speeds at different heights are different, when a blade is rotating at a plane, it actually receives the harmonic force from wind.
Therefore, the peordic loads are produced to influence the turbines.

## Slide 7: Motivation2
Challenges for wind turbine control:
Model uncertainties
Periodic loads on blades
Coupling dynamics of 3-bladed pitch system
Difficulties in designing controller:
Operating point varies constantly – actual dynamics is different from nominal model
Source: Liebherr
Objective:
Speed and power regulation in high wind speeds
Mitigate periodic loads
Robust stability and robust performance
Potential solution: Robust Controller (structured singular values ()-synthesis)
Notes: One potential solution is

## Slide 8: Outline
Background
Research Objective
Proposed Robust Control Method
Concluding Remarks
Future Tasks

## Slide 9: Dynamics and modeling
Bir, G.S., 2010. User's guide to MBC3: Multi-blade coordinate transformation code for 3-bladed wind turbine.
An average state-space system is obtained from the complete set of linearizations at N azimuth angles by computing
A series of LTI state space model depends on azimuth
e.g. 36 models: = 0, 10, 20,…350 deg
Periodic LTV state space model
Steady state: blade motion is a Fourier series equation
linearization
MBC transformation
Modeling including periodic dynamics
transform from rotating coordinates to nonrotating coordinates
Notes: The dynamics of wind turbine rotor blades are generally expressed in rotating frames attached to the
individual blades. The tower-nacelle subsystem sees the combined effect of all rotor blades, not the
individual blades. This is because the rotor responds as a whole to excitations such as aerodynamic gusts,
control inputs, and tower-nacelle motion—all of which occur in a nonrotating frame. Multi-blade
coordinate transformation (MBC) helps integrate the dynamics of individual blades and express them in a
fixed (nonrotating) frame. MBC involves two steps: transformation of the rotating degrees of freedom,
and transformation of the equations of motion.
MBC transformation can reduce the variations between linearizations obtained at different azimuths, and therefore yields a better representation of the turbine dynamics

## Slide 10: Uncertain model structures
Frequency responses comparison
Model mismatch in high frequency regions
Uncertain model structure formulation
Fit an uncertain model structure to an array of LTI responses :
Pick nominal model: 18 m/s
LTI state space model
Challenge: wind speed changes so actual dynamics changes
Uncertain model structures
14 m/s, 16 m/s, 20 m/s, and 22 m/s

## Slide 11: Shear components
Bode Diagram has large magnitude
Horizontal and vertical wind shear effects to dynamic modeling
Include wind shear components in the model
Magnitude of , to moments , :
70 – 80 dB
Magnitude of horizontal wind to moments , :
20 – 30 dB

## Slide 12: Control architecture formulation
Control architecture formulation
Collective loop:
Speed and power regulation
GSPI/DOB [1]
Individual loop:
Periodic load mitigation
Robust control with weighting function selection
[1] Yuan, Y., Chen, X., and Tang, J., 2017, "Disturbance Observer-Based Pitch Control of Wind Turbines for Enhanced Speed Regulation," Journal of Dynamic Systems, Measurement, and Control, V139(7), pp. 071006.
Notes: We plan to use individual control to tracle this problem. The upper control loop is the collective loop, the lower loop is the individual loop.

## Slide 13: Structural singular value (-synthesis formulation
RSRP (robust stability and robust performance) guarantee under model uncertainties due to operating point variation
Disturbance rejection via weighting function selection
Advantages using structural singular value-synthesis
The performance of MIMO control systems are characterized using norms
: disturbance
: input
:output
: weighted output
G: generalized plant
K: robust controller
: perturbation of G
M- structure

## Slide 14: Power spectral density
Power spectral density (PSD) of blade 1 root flapwise moment with only collective loop
Multiple peaks at 1P (per revolution), 2P, 3P, … frequencies due to periodic loads on
1P
2P
3P
4P
Rated rotor speed:
Severe limits:
Component failure

## Slide 15: Weighting functions
Rotating coordinate | Non-rotating coordinate
1P | 0P @ and
2P | 3P@ and
3P | 3P @
4P | 3P@ and
5P | 6P@ and
6P | 6P@
7P | 6P@ and
Rotating coordinate | Non-rotating coordinate
1P | 
2P | 
3P | 
4P | 
5P | 
6P | 
7P | 
Sensitivity function
Minimize the norm
Frequency effects change due to coordinates change
Further penalize the control input and output performance

## Slide 16: Weighting functions
Select weighting functions
low frequency
low pass filter

## Slide 17: Singular values
Multivariate transfer functions: singular values of transfer function
Open-loop and closed-loop responses of the nonlinear wind turbine under turbulent wind excitations
Deal with uncertain model structure (a group of curves)
0P and 3P disturbance rejection
= 0.1784 < 1 RSRP guaranteed
Notes: The shaping of multivariate transfer functions is based on the idea that a satisfactory definition of gain for a matrix transfer function is given by the singular values of the transfer function

## Slide 18: Outline
Background
Research Objective
Proposed Robust Control Method
Concluding Remarks
Future Tasks

## Slide 19: PSD results
PSD result analysis at multiple frequencies
18 m/s turbulent wind field excitation
Significant 1P, 2P, and 4P peak reduction

## Slide 20: Load analysis
Blade and tower fatigue damage equivalent load (DEL) comparison
Collective control
PID individual control
Robust individual control
Blade flapwise: Robust: -20% of PID
Blade edgewise: same level
Tower base fore-aft: 3%-10% decrease
Tower base side-side: same level
(DEL: industrial standard)

## Slide 21: Concluding remarks
A robust controller with mu synthesis for wind turbine is developed;
Individual pitch control is utilized to reject periodic loads;
Robust control strategy is formulated to tackle with modeling uncertainties;
Periodic loads on blades are significantly reduced.